Building Applications – Standard Conditions

General	1

Public Buildings	1

Food Premises	3

Skin Penetration	3

Hairdressing	3

# General

- Toilets to be mechanically ventilated in compliance with the Sewerage (Lighting, Ventilation and Construction) Regulations 1971.

# Public Buildings

The premises must comply with the provisions of the Health (Public Buildings) Regulations 1992, however please pay particular attention to the following conditions:

- Designated exits must be fitted with illuminated exist signs compliant with AS 2293.

- Exit doors are required to open in the direction of egress.

- Exit doors are to be provided with approved single downward hand action locks such that exit doors can always be opened from the interior

- NO ESCAPE” signs in letters not less that 100mm high and 12mm wide are to be provided to doors (#) as marked on the site plans.

- Mechanically ventilation must be provided in accordance with AS1668.2 – Mechanical Ventilation for Acceptable Indoor Air Quality, alternatively the building may be naturally ventilated in accordance with the Building Regulations.

- The internal public areas must be illuminated to 40 lux and distributed over at least 2 final sub-circuits with an overriding “ON” switch located near the main entrance.

- Toilets must be illuminated to 80 lux. (reg28&38).

- Globes less than 2.4m from the floor must not be exposed and need to be protected from accidental contact or damage.

- Every classroom, lecture theatre, drawing room, laboratory, manual training room, assembly hall or any other teaching area shall be provided with an artificial lighting system capable of providing the illumination recommended in relation to such an area under Australian Standard 1680 – Code of Practice for Interior Lighting and the Visual Environment.

- Safety lighting is to be provided to foyers, passages, ramps, each step tread & main aisles between blocks of fixed seats of any area open to the public when normal lighting is dimmed or extinguished.

- External areas must be illuminated to 1 lux, the circuits must be separate to any internal circuits and distributed over at least 2 final sub-circuits.

Emergency lighting must be provided and maintained in accordance with the BCA and AS/NZS 2293.

- Sanitary conveniences are to be marked with signage to indicate which gender they are intended for.

- Sanitary convenience signs shall be illuminated during the hours of darkness while open to the public.

- Approved illumination shall be provided to all access areas leading to external sanitary conveniences.

- All seats used for seating audiences in a public building shall be securely fixed to the floor unless fastened together in groups of not less than 4 seats.

- Curtains and decorative treatments must be made of non-toxic fire retardant materials.

- Any room or enclosure in which batteries with a stored capacity exceeding 1 kw/h or with a floating voltage exceeding 115 shall conform to the installation requirements of Australian Standard 2676 — Installation and Maintenance of Batteries in Buildings.

- The electrical switchboard must be labeled, secured to prevent public access, and not located at or near an emergency exit.

- Every raised area, which may present a hazard, shall be provided with an enclosing wall or guardrail. Steps and landings shall be provided with handrails on each side that is not stepped.

- All stairs must be constructed so that treads are at least 280mm wide and risers are no more than 180mm high.

- All balustrades are to be constructed so that the verticals are less than 125mm apart.

- Electric fans, other than ceiling fans, in any area of a public building to which members of the public have access shall be installed in a permanent position and so that the blades of the fan are —

  - Not less than 2000 mm above floor level; and

  - Protected by a robust guard.

- Ceiling fans shall be installed so that the blades are not less than 2400mm above the floor level unless the blades are protected by guards that prevent accidental contact with them.

- Radiant electrical heaters shall be installed in a fixed position and so every part of the heating element is not less than 2100 mm from the level of the floor and not less than 600 mm from any ceiling that is made of a combustible material.

- A Certificate of Electrical Compliance (Form 5) must be completed by a licensed electrical contractor, certifying that the electrical work of the public building conforms with the relevant provisions of the Health (Public Buildings) Regulations 1992, the Building Code of Australia and the Electricity Act 1945.

- Once construction has been completed, application is to be made to the Local Government for a Certificate of Approval (Form 2) in accordance with the Health (Public Buildings) Regulations 1992.

- Where seats are arranged in regular rows of 10 to 42 seats aisles shall be provided on both sides of each row.

# Food Premises

# Skin Penetration

# Hairdressing